Tender text CENTRAX CU3000

Transparent power quality and energy consumption monitoring

The CENTRAX CU3000 combines the functionality of a highly accurate instrument for heavy current applications with the possibilities of a freely programmable Soft-PLC in one housing. The connection of the process environment may be performed by communication interfaces, via digital I/Os, analog outputs or relays.

PLC functionality

- Based on Codesys, 3 performance classes

- BASIC: Flexible processing of the data of the measurement device using the complete I/O functionality

- ADVANCED: BASIC + Modbus RTU/TCP master and time-dependent processes

- PROFESSIONAL: ADVANCED + self-defined websites and local visualizations + Codesys data logger

Condition monitoring

- Provision of all voltages, currents, powers, power factors

- Variance of system variables with time reference

- Measurements of Modbus slaves

Energy flow analysis

- Power  mean-values with trend-analysis for preventing load-peaks

- Load profile storage with fluctuation range (min/max) per interval

- Active energy class 0.2S, Reactive energy class 0.5S  (HT/LT, demand/delivery), configurable resolution

- Further mean-values and meters with selectable base quantity

Power quality analysis

- Harmonic analysis acc. IEC 61000-4-7

- Assessment of voltage and current imbalance

- Phasor and phase sequence display for connection check

- Waveform display

- Optional disturbance recorder for PQ events (voltage dip, swell, interruption) acc. IEC 61000-4-30 Ed.3 with RMS1/2 and waveform recordings

Hardware options

Up to 4 modular extensions: Analog outputs ±20mA (2/4), relay outputs (2), digital inputs (4) active / passive, GPS time synchronization, fault-current monitoring (residual or earth current), temperature monitoring (Pt100, PTC), IEC61850

Communication

- Ethernet (Modbus/TCP, http/https, NTP, SFTP, SYSLOG)

- Modbus/RTU master or slave

- Optional: IEC61850

- Scheduled data export to SFTP server

Security

- Flexible Role Based Access Control

- Encrypted communication via HTTPS

- Audit Log records all security related procedures, support for SYSLOG for transfer to central network monitoring server

- Client whitelist: IP address list for restricting authorized computers

- Digital firmware signature: Prevents that manipulated firmware gets into the device via update

Further features

- 4 current and 4 voltage channels with 0.1% accuracy, direct measurement or via transformers

- Measurement category 600V, CAT III (voltage), 300V,CAT III (current)

- Optional UPS (5x3 minutes)

- Data logger with16 GB data memory (option)

- Sampling rate: 18kHz

- Monitoring and alarming via limit values and monitoring functions

- For panel mounting 144x144mm

- Identical operation as devices of the AM/PQ/DM series

Manufacturer

Camille Bauer Metrawatt AG

Aargauerstrasse 7

CH-5610 Wohlen

https://www.camillebauer.com/