Tender text LINAX PQ5000-MOBILE

Transparent power quality and energy consumption monitoring
The LINAX PQ5000-MOBILE combines the characteristics of a normative power quality measurement device with functions for energy consumption and condition monitoring. Different versions for current measurement via clamps or Rogowski coils are available.

The modern, multi-lingual design allows operating and parameterizing the device via website (LAN or WLAN). The integrated webserver provides remote acquisition, visualization and analysis of measured data. No additional software is required.

Power quality analysis

The device is intended to be used for a power quality assessment according IEC 61000-4-30 Ed.3 in class A. The recorded events (voltage sag, voltage swell, voltage interruption, RVC, current swell, frequency change and homopolar voltage) serve both to prove that disturbances have occurred and to search for the origin of the disturbance in order to increase security of supply. Using the statistical voltage and current quantities, compliance with supply contracts or internal requirements can be verified. Assessment according EN 50160, IEC 61000-2-2/4/12, IEEE 519, GB/T or self-defined limits can be carried out after the measurement, corresponding conformity reports can be created via the device website (PQEasy-Report).

- Independent certification acc. IEC 62586-2 by Federal Institute of Metrology METAS

- Support for standardized, manufacturer independent PQDIF format acc. IEEE 1159.3

- Definable event recording duration: Up to 6 seconds for samples and 3 minutes for RMS values

- Event display via website with time zooming function and reading of values

Energy flow analysis

- Power  mean-values with trend-analysis for preventing load-peaks

- Load profile storage with fluctuation range (min/max) per interval

- Active energy, Reactive energy class, demand and supply, configurable resolution

- Further mean-values and meters with selectable base quantity

Options

GPS time synchronization, Current measurement via clamps or Rogowski coils

Communication

- Ethernet (Modbus/TCP, http/https, NTP, SFTP, SYSLOG)

- WLAN Access Point

- Scheduled data export (CSV and PQDIF files) to SFTP server

Security

- Flexible Role Based Access Control

- Encrypted communication via HTTPS

- Audit Log records all security related procedures, support for SYSLOG for transfer to central network monitoring server

- Client whitelist: IP address list for restricting authorized computers

- Digital firmware signature: Prevents that manipulated firmware gets into the device via update

Further features

- 4 current and 4 voltage channels

- Measurement category 600V  CAT III (voltage), 300V CAT IV (current)

- Standard: UPS (5x3 minutes)

- 16 GB memory, data storage up to 3 years

- Sampling rate: 18kHz

- Monitoring and recording using user-defined limit values and monitoring functions

- Configuration manager covering up to 20 sites

- Dimensions 25 x 23 x 12cm, waterproof (IP64) if housing is closed

Manufacturer

Camille Bauer Metrawatt AG

Aargauerstrasse 7

CH-5610 Wohlen

https://www.camillebauer.com/