Tender SIRAX BM1200

Programmable unit with display for heavy current monitoring

For the measurement, monitoring and analysis of power networks

Netform			Single phase, 2-wire-Net

Three phase, 3-/4-wire-Net unbalanced load

Measurement input			Nominal voltage 57,7…277VLN, 100…480VLL

Nominal currant 1…5A (max. 6A)

45…65Hz

Protection class			II

Measurement category	CATIII 300V

Basic values	Current, neutral current (calculated), voltage, frequency, active / apparent power, power, factors, Min. / Max. Values current / voltage, phase angle

Counter	Active energy Cl.1,0, reactive energy Cl.2, import/export, meters

Network analysis			THD_U, THD_I

Uncerainty 			U,I: 0,5%; P,Q,S: 0,5%; THD: 2,0%

Inputs/Outputs			Pulse output

Interface			Modbus/RTU (RS485)

Measured value display	LCD-Display

Parameterization			via pushbutton or Modbus/RTU

Power supply			60…300V AC/DC

Housing	Housing for panel mounting 96x96 (front), installation depth 35mm or 55mm, IP50 (front), IP20 (housing/terminals), UL94 V-0

Type			SIRAX BM1200

Manufacturer			Camille Bauer Metrawatt AG

Aargauerstrasse 7

CH-5610 Wohlen

http://www.camillebauer.com