Tender SIRAX BM1450

Multifunctional DC Energy Meter

For the determination of voltage, current, power, capacity and energy

Input voltage			Nominal input range 10…60V / 61…200V / 201…1000V

Operating measuring range 2…125% of nominal value

Nominal input burden <0.4W

Overload indication >126% of nominal value

Max continuous input 125% of nominal value

Overload withstand 2 x rated value (1s application repeated 10 times at 10s interval)

Input current			Full scale setting range 1…20kA

Numbers of channels 4

Current sensor External

Shunt setting range 50…150mV

Operating measuring range 2…125% of nominal value

Nominal input burden <0.1W per channel

Overload indication >126% of nominal value

Max continuous input 125% of nominal value

Overload withstand 20 x rated value (1s application repeated 5 times at 5min interval)

Power supply			60…300VAC/DC

Frequency 			45…65Hz

Basic values			DC voltage, current, power, Energy

Uncerainty			voltage, current and power 0.5%; Energy class 1

Protection class			II

Measurement category	1000V CATII, 600V CATIII (measuring inputs)

300V CATIII (power supply)

Degree of pollution		2

Outputs		4 relay output freely selectable for limit, pulse or timer

Interface			Modbus/RTU (RS485)

Measured value display	4 line, 8 digit LED display

Parameterization			via pushbutton or Modbus/RTU

Housing	Housing for panel mounting 96x96 (front), installation depth 80mm, IP50 (front), IP20 (housing/terminals), UL94 V-0

Material	Polycarbonate

Type			SIRAX BM1450

Hersteller			Camille Bauer Metrawatt AG

Aargauerstrasse 7

CH-5610 Wohlen

http://www.camillebauer.com